## DETAIL
Estimate of Materials and Cost of Construction
[11 empty] | Summary | Amount
[11 empty] | Subtotal | 271816.1684
[11 empty] | Profit/Overhead | 81544.8505
[11 empty] | Total | 353361.0189
Item # | Ref. Sheet | CSI Ref. | Description | Unit | Quantity | Wastage | Quantity w/ Wastage | Unit Material Cost | Total Material Cost | Unit Labor Cost | Total Labor Cost | Total Item Cost | Trade Cost
|  | DIV-01 | GENERAL | [9 empty] | 119000
1 |  |  | Permit | LS | 1 | 0% | 1 | 0 | 0 | 0 | 0 | 15000
2 |  |  | Supervision | LS | 1 | 0% | 1 | 0 | 0 | 0 | 0 | 8000
3 |  |  | Final Cleanup | LS | 1 | 0% | 1 | 0 | 0 | 0 | 0 | 9000
4 |  |  | Mobilization Cost | LS | 1 | 0% | 1 | 0 | 0 | 0 | 0 | 14000
5 |  |  | Project Overheads | LS | 1 | 0% | 1 | 0 | 0 | 0 | 0 | 16000
6 |  |  | Bonds | LS | 1 | 0% | 1 | 0 | 0 | 0 | 0 | 18000
7 |  |  | Fees (Architect & Engineer) | LS | 1 | 0% | 1 | 0 | 0 | 0 | 0 | 12000
8 |  |  | Temporary Control & Facilities | LS | 1 | 0% | 1 | 0 | 0 | 0 | 0 | 12000
9 |  |  | Testing & Balancing | LS | 1 | 0% | 1 | 0 | 0 | 0 | 0 | 15000
|  | DIV-02 | Site Work/Existing Conditions | [9 empty] | 5891.4091
Demolition Work
M-101 M-103
Building-04 (Ll-3)
10 |  |  | Remove (24" X 6") Existing Duct | LF | 88.47 | 0% | 88.47 | 0 | 0 | 14.33 | 1267.7751 | 1267.7751
11 |  |  | Remove (24" X 8") Existing Duct | LF | 59.19 | 0% | 59.19 | 0 | 0 | 14.33 | 848.1927 | 848.1927
12 |  |  | Remove (18" X 8") Existing Duct | LF | 12.76 | 0% | 12.76 | 0 | 0 | 12.7 | 162.052 | 162.052
13 |  |  | Patch Duct Main | LF | 99.84 | 0% | 99.84 | 0 | 0 | 9.42 | 940.4928 | 940.4928
14 |  |  | Disconnect Duct From Diffuser | EA | 4 | 0% | 4 | 0 | 0 | 130 | 520 | 520
15 |  |  | Remove And Salvage Thermostat For Reuse | EA | 1 | 0% | 1 | 0 | 0 | 90 | 90 | 90
16 |  |  | Disconnect And Remove Existing Air Compressor And Receivers. Disconnect Piping At Nearest Isolation Valve | EA | 2 | 0% | 2 | 0 | 0 | 250 | 500 | 500
Building-05 (Service Level)
M-102
17 |  |  | Remove (10" X 6") Existing Duct | LF | 12.77 | 0% | 12.77 | 0 | 0 | 10.72 | 136.8944 | 136.8944
18 |  |  | Remove (6" X 6") Existing Duct | LF | 29.37 | 0% | 29.37 | 0 | 0 | 9.34 | 274.3158 | 274.3158
19 |  |  | Remove (8" X 10") Existing Duct | LF | 3.44 | 0% | 3.44 | 0 | 0 | 10.04 | 34.5376 | 34.5376
20 |  |  | Remove (8" X 8") Existing Duct | LF | 7.05 | 0% | 7.05 | 0 | 0 | 1.014 | 7.1487 | 7.1487
21 |  |  | Remove Existing Fsd And Associated Actuator Linkage | EA | 2 | 0% | 2 | 0 | 0 | 145 | 290 | 290
22 |  |  | Remove Existing Air Filter | EA | 3 | 0% | 3 | 0 | 0 | 100 | 300 | 300
23 |  |  | Disconnect Duct From Duct/Filter | EA | 4 | 0% | 4 | 0 | 0 | 130 | 520 | 520
|  | DIV-23 | Hvac/Mechanical | [9 empty] | 146924.7593
Building-04 (Ll-3/E-Level)
M-104
Duct Work/Miscellaneous Fixtures
24 |  |  | (12" X 14") Duct With Insulation - Attached To Structure W/ Hanger Strap, Self Tapping Screws Attached To Duct And Hilti Hdi-P Drop In Anchor (3/8" Dia) Attached To Concrete Slab | LF | 15.87 | 5% | 16.6635 | 20.41 | 340.102 | 42.6 | 709.8651 | 1049.9671
25 |  |  | (18" X 14") Duct With Insulation - Attached To Structure W/ Hanger Strap, Self Tapping Screws Attached To Duct And Hilti Hdi-P Drop In Anchor (3/8" Dia) Attached To Concrete Slab | LF | 8.78 | 5% | 9.219 | 37.33 | 344.1453 | 78.19 | 720.8336 | 1064.9789
26 |  |  | (22" X 14") Duct With Insulation - Attached To Structure W/ Hanger Strap, Self Tapping Screws Attached To Duct And Hilti Hdi-P Drop In Anchor (3/8" Dia) Attached To Concrete Slab | LF | 9.37 | 5% | 9.8385 | 42.06 | 413.8073 | 87.35 | 859.393 | 1273.2003
27 |  |  | (24" X 12") Duct With Insulation - Attached To Structure W/ Hanger Strap, Self Tapping Screws Attached To Duct And Hilti Hdi-P Drop In Anchor (3/8" Dia) Attached To Concrete Slab | LF | 11.34 | 5% | 11.907 | 50.36 | 599.6365 | 94.84 | 1129.2599 | 1728.8964
28 |  |  | 14" Dia Duct With Insulation - Attached To Structure W/ Hanger Strap, Self Tapping Screws Attached To Duct And Hilti Hdi-P Drop In Anchor (3/8" Dia) Attached To Concrete Slab | LF | 8.42 | 5% | 8.841 | 26.2 | 231.6342 | 64.11 | 566.7965 | 798.4307
29 |  |  | (34" X 14") Duct With Insulation - Attached To Structure W/ Hanger Strap, Self Tapping Screws Attached To Duct And Hilti Hdi-P Drop In Anchor (3/8" Dia) Attached To Concrete Slab | LF | 4.13 | 5% | 4.3365 | 65.33 | 283.3035 | 114.72 | 497.4833 | 780.7868
30 |  |  | 45 Degree Bend @ Duct | EA | 6 | 0% | 6 | 144 | 864 | 97 | 582 | 1446
31 |  |  | Transition @ Duct To Duct | EA | 3 | 0% | 3 | 193 | 579 | 128 | 384 | 963
32 |  |  | Connection Of (18" X 14") Duct To Main Duct | EA | 1 | 0% | 1 | 224 | 224 | 140 | 140 | 364
33 |  |  | 34" Wide Flexible Duct/Connection | EA | 1 | 0% | 1 | 157 | 157 | 98 | 98 | 255
34 |  |  | Cap Existing Duct | EA | 4 | 0% | 4 | 87 | 348 | 140 | 560 | 908
35 |  |  | Volume Damper | EA | 4 | 0% | 4 | 168 | 672 | 106 | 424 | 1096
36 |  |  | Fire Damper | EA | 1 | 0% | 1 | 190 | 190 | 120 | 120 | 310
Pipe Work/Miscellaneous Fixtures
37 |  |  | 1-1/2" Chilled Water Supply/Return Pipe With Insulation - Attached To Concrete Slab With Unistrut Channels And Hanger Rod | LF | 394.58 | 5% | 414.309 | 18.77 | 7776.5799 | 34.1 | 14127.9369 | 21904.5168
38 |  |  | 1" Chilled Water Supply/Return Pipe With Insulation - Attached To Concrete Slab With Unistrut Channels And Hanger Rod | LF | 48.34 | 5% | 50.757 | 11.33 | 575.0768 | 22.96 | 1165.3807 | 1740.4575
39 |  |  | Provide Rls Condensate Piping Complete In All Respects - Attached To Concrete Slab With Unistrut Channels And Hanger Rod | LF | 112.34 | 5% | 117.957 | 14.2 | 1674.9894 | 27.35 | 3226.124 | 4901.1133
40 |  |  | 1/2" Condensate Drain Pipe - Attached To Concrete Slab With Unistrut Channels And Hanger Rod | LF | 16.76 | 5% | 17.598 | 6.06 | 106.6439 | 14.12 | 248.4838 | 355.1276
41 |  |  | 90 Degree Bend @ 1-1/2" Chilled Water Pipe | EA | 10 | 0% | 10 | 147 | 1470 | 98 | 980 | 2450
42 |  |  | 90 Degree Bend @ 1" Chilled Water Pipe | EA | 4 | 0% | 4 | 120 | 480 | 84 | 336 | 816
43 |  |  | 90 Degree Bend @ Rls Condensate Pipe | EA | 10 | 0% | 10 | 103 | 1030 | 75 | 750 | 1780
44 |  |  | 90 Degree Bend @ 1/2" Condensate Drain Pipe | EA | 1 | 0% | 1 | 94 | 94 | 52 | 52 | 146
45 |  |  | T Connection @ Rls Condensate Pipe | EA | 2 | 0% | 2 | 138 | 276 | 90 | 180 | 456
46 |  |  | Transition @ 1-1/2" To 1" Chilled Water Pipe | EA | 2 | 0% | 2 | 156 | 312 | 112 | 224 | 536
47 |  |  | Condensate Drain Pan | EA | 1 | 0% | 1 | 197 | 197 | 130 | 130 | 327
48 |  |  | Provide 3/4" Gate Valve | EA | 2 | 0% | 2 | 142 | 284 | 103 | 206 | 490
49 |  |  | Provide 3/4" Gate Valve @ Chilled Water Pipe And Connect To Walk In Freezer Refrigeration Condensing Unit Equipment | EA | 4 | 0% | 4 | 142 | 568 | 103 | 412 | 980
50 |  |  | Provide Full Port Ball Valve And Wet Tap | EA | 2 | 0% | 2 | 260 | 520 | 145 | 290 | 810
Mechanical Fixtures
51 |  |  | Install Refrigeration Equipment Condensing Unit For Walk In Freezer And Refrigerated Box - Mount Condensing Unit On Etr Housekeeping Pad - Mount Evaporators At Walk In Box Ceiling - Provide All Control Wiring And Refrigerant Line Sets Per Manufacturer'S Requirements - Freezer Box: 3/8" Liquid, 7/8" Suction - Refrigerated Box: 5/8" Liquid, 7/8" Suction | EA | 2 | 0% | 2 | 2612 | 5224 | 1439 | 2878 | 8102
52 |  |  | (18"H X 33"W X 40"D) Hvac Equipment Ac-1 With Following Details; - Equipment Type: Ducted Fan Coil - Manf: Trane, Model: Bchd036 - Rating: 03 Ton, Total Cooling Capacity: 38,000 Btuh - Supply Air Flow: 1,400 Cfm, Water Flow Rate: 10 Gpm - Attached To Concrete Slab With 3/8"-16 Anvil (Fig 146)Threaded Rod (08 Ea), Hanger Mount Vibration Isolator; Spring Solator Type Mason Or Approved Equal (04 Ea) And 3/8" Hilti Hdi-P Drop In Anchor (08 Ea) - (33" X 40") Drain Pan @ Bottom Of Unit Attached To Hangers | EA | 1 | 0% | 1 | 4420 | 4420 | 2316 | 2316 | 6736
53 |  |  | Pressure Gauge With Needle Stop Valve | EA | 2 | 0% | 2 | 294 | 588 | 162 | 324 | 912
54 |  |  | Thermometer | EA | 2 | 0% | 2 | 213 | 426 | 104 | 208 | 634
55 |  |  | 3/4" Drain Valve With Hose Bib | EA | 2 | 0% | 2 | 156 | 312 | 100 | 200 | 512
56 |  |  | 1-1/4" Two Way Motorized Valve | EA | 1 | 0% | 1 | 235 | 235 | 128 | 128 | 363
57 |  |  | Balancing Valve | EA | 1 | 0% | 1 | 168 | 168 | 102 | 102 | 270
58 |  |  | Y Strainer | EA | 1 | 0% | 1 | 190 | 190 | 118 | 118 | 308
59 |  |  | Isolation Valve | EA | 2 | 0% | 2 | 166 | 332 | 105 | 210 | 542
60 |  |  | 34" Wide Air Filter @ Ac-1 | EA | 1 | 0% | 1 | 312 | 312 | 160 | 160 | 472
61 |  |  | Condensate Pump Cp-1 With Following Details; - Model Number: Vcmx-20Uls - Discharge Size: 1/4" Fnpt X 3/8" Od Barbed - Cord Length: 06 Feet, Weight: 5.5 Lb - It Will Have Automatic Start/Stop Capacity | EA | 1 | 0% | 1 | 2492 | 2492 | 1493 | 1493 | 3985
62 |  |  | Side Register (1,500 Cfm) | EA | 1 | 0% | 1 | 386 | 386 | 212 | 212 | 598
63 |  |  | Duct Mounted Diffuser/Grill With The Following Details; - Duct Size: 14" Dia, Cfm: 700 - Manf: Titus, Model: R-Omni | EA | 4 | 0% | 4 | 347 | 1388 | 193 | 772 | 2160
64 |  |  | Duct Mounted Diffuser/Grill With The Following Details; - Duct Size: (24" X 12"), Cfm: 850 - Manf: Titus, Model: 350 Rl | EA | 1 | 0% | 1 | 419 | 419 | 246 | 246 | 665
65 |  |  | Duct Mounted Diffuser/Grill With The Following Details; - Duct Size: (24" X 12"), Cfm: 550 - Manf: Titus, Model: 350 Rl | EA | 1 | 0% | 1 | 390 | 390 | 228 | 228 | 618
66 |  |  | Provide Space Temperature Sensor And Extend Cat6-E To Existing Bms Panel | EA | 2 | 0% | 2 | 268 | 536 | 132 | 264 | 800
67 |  |  | Provide Thermostat Zone Sensor For Fan Coil Unit Ac-1 | EA | 1 | 0% | 1 | 146 | 146 | 95 | 95 | 241
68 |  |  | Reinstall Existing Thermostat For Reheat Coil (Labor Only) | EA | 1 | 0% | 1 | 0 | 0 | 95 | 95 | 95
Others
69 |  |  | Provide Bms Wiring To Etr Bms Panel For Termination At Bms Panel And Bms Program Changes Including Graphic Update | LF | 50 | 5% | 52.5 | 8.77 | 460.425 | 20.33 | 1067.325 | 1527.75
70 |  |  | Core Drill Slab Down To E-Level For 1-1/2" Chilled Water Pipe | EA | 2 | 0% | 2 | 68 | 136 | 234 | 468 | 604
Building-05 (Service Level)
M-106 M-107
Duct Work/Miscellaneous Fixtures
71 |  |  | (8" X 8") Duct With Insulation - Attached To Structure W/ Hanger Strap, Self Tapping Screws Attached To Duct And Hilti Hdi-P Drop In Anchor (3/8" Dia) Attached To Concrete Slab | LF | 8.85 | 5% | 9.2925 | 12.68 | 117.8289 | 27.3 | 253.6853 | 371.5142
72 |  |  | (8" X 6") Duct With Insulation - Attached To Structure W/ Hanger Strap, Self Tapping Screws Attached To Duct And Hilti Hdi-P Drop In Anchor (3/8" Dia) Attached To Concrete Slab | LF | 12.58 | 5% | 13.209 | 11.95 | 157.8476 | 26.02 | 343.6982 | 501.5457
73 |  |  | (10" X 10") Duct With Insulation - Attached To Structure W/ Hanger Strap, Self Tapping Screws Attached To Duct And Hilti Hdi-P Drop In Anchor (3/8" Dia) Attached To Concrete Slab | LF | 6.07 | 5% | 6.3735 | 13.44 | 85.6598 | 29.36 | 187.126 | 272.7858
74 |  |  | (12" X 14") Duct With Insulation - Attached To Structure W/ Hanger Strap, Self Tapping Screws Attached To Duct And Hilti Hdi-P Drop In Anchor (3/8" Dia) Attached To Concrete Slab | LF | 26.05 | 5% | 27.3525 | 20.41 | 558.2645 | 42.6 | 1165.2165 | 1723.481
75 |  |  | (24" X 10") Duct With Insulation - Attached To Structure W/ Hanger Strap, Self Tapping Screws Attached To Duct And Hilti Hdi-P Drop In Anchor (3/8" Dia) Attached To Concrete Slab | LF | 17.71 | 5% | 18.5955 | 49.92 | 928.2874 | 90.61 | 1684.9383 | 2613.2256
76 |  |  | (44" X 10") Duct With Insulation - Attached To Structure W/ Hanger Strap, Self Tapping Screws Attached To Duct And Hilti Hdi-P Drop In Anchor (3/8" Dia) Attached To Concrete Slab | LF | 4.98 | 5% | 5.229 | 84.2 | 440.2818 | 141.6 | 740.4264 | 1180.7082
77 |  |  | 90 Degree Bend @ (10"X10") Duct | EA | 1 | 0% | 1 | 168 | 168 | 120 | 120 | 288
78 |  |  | 90 Degree Bend @ (12"X14") Duct | EA | 1 | 0% | 1 | 190 | 190 | 103 | 103 | 293
79 |  |  | 45 Degree Bend @ (8"X6") Duct | EA | 4 | 0% | 4 | 142 | 568 | 81 | 324 | 892
80 |  |  | Cap Existing Duct Work | EA | 2 | 0% | 2 | 87 | 174 | 140 | 280 | 454
81 |  |  | Flexible Connection (44" Width) I/C Clips On Both Sides | EA | 1 | 0% | 1 | 157 | 157 | 98 | 98 | 255
82 |  |  | Connection Of New Duct To Existing Duct | EA | 2 | 0% | 2 | 224 | 448 | 140 | 280 | 728
83 |  |  | Volume Damper | EA | 7 | 0% | 7 | 168 | 1176 | 106 | 742 | 1918
84 |  |  | 1.5 Hr Fire Damper | EA | 1 | 0% | 1 | 190 | 190 | 120 | 120 | 310
Pipe Work/Miscellaneous Fixtures
85 |  |  | 1-1/2" Chilled Water Supply/Return Pipe With Insulation - Attached To Concrete Slab With Unistrut Channels And Hanger Rod | LF | 30.11 | 5% | 31.6155 | 18.77 | 593.4229 | 34.1 | 1078.0886 | 1671.5115
86 |  |  | 3/4" Chilled Water Supply/Return Pipe With Insulation - Attached To Concrete Slab With Unistrut Channels And Hanger Rod | LF | 95.85 | 5% | 100.6425 | 7.35 | 739.7224 | 14.59 | 1468.3741 | 2208.0964
87 |  |  | 5/8" Chilled Water Supply/Return Pipe With Insulation - Attached To Concrete Slab With Unistrut Channels And Hanger Rod | LF | 10.48 | 5% | 11.004 | 6.47 | 71.1959 | 13.6 | 149.6544 | 220.8503
88 |  |  | Provide Rls Condensate Piping Complete In All Respects - Attached To Concrete Slab With Unistrut Channels And Hanger Rod | LF | 20 | 5% | 21 | 14.2 | 298.2 | 27.35 | 574.35 | 872.55
89 |  |  | 1/2" Condensate Drain Pipe - Attached To Concrete Slab With Unistrut Channels And Hanger Rod | LF | 43.3 | 5% | 45.465 | 86 | 3909.99 | 35 | 1591.275 | 5501.265
90 |  |  | 90 Degree Bend @ 1-1/2" Chilled Water Pipe | EA | 6 | 0% | 6 | 147 | 882 | 98 | 588 | 1470
91 |  |  | 90 Degree Bend @ 3/4" Chilled Water Pipe | EA | 4 | 0% | 4 | 102 | 408 | 80 | 320 | 728
92 |  |  | 90 Degree Bend @ 5/8" Chilled Water Pipe | EA | 2 | 0% | 2 | 113 | 226 | 72 | 144 | 370
93 |  |  | T Connection @ Chilled Water Pipe (3/4" To 5/8") | EA | 2 | 0% | 2 | 138 | 276 | 90 | 180 | 456
94 |  |  | T Connection @ Chilled Water Pipe (1-1/2" To 3/4") | EA | 4 | 0% | 4 | 156 | 624 | 102 | 408 | 1032
95 |  |  | Transition Of Chilled Water Pipe (1-1/2" To 3/4") | EA | 2 | 0% | 2 | 156 | 312 | 102 | 204 | 516
96 |  |  | 90 Degree Bend @ 1/2" Condensate Pipe | EA | 3 | 0% | 3 | 95 | 285 | 40 | 120 | 405
97 |  |  | T Connection @ 1/2" Condensate Pipe | EA | 1 | 0% | 1 | 120 | 120 | 76 | 76 | 196
98 |  |  | Provide 3/4" Gate Valve | EA | 6 | 0% | 6 | 142 | 852 | 103 | 618 | 1470
99 |  |  | Provide Full Port Ball Valve And Wet Tap | EA | 2 | 0% | 2 | 260 | 520 | 145 | 290 | 810
Mechanical Fixtures
100 |  |  | Install Refrigeration Equipment For Walk In Freezer - Suspend Walk In Freezer And Refrigerator Condensing Units Above Walk In Box Ceiling - Mount Evaporator At Walk In Box Ceiling - Provide All Control Wiring And Refrigerant Line Sets Per Manufacturer'S Requirements - Freezer Box: 3/8" Liquid, 7/8" Suction - Refrigerated Box: 5/8" Liquid, 7/8" Suction | EA | 2 | 0% | 2 | 2612 | 5224 | 1439 | 2878 | 8102
101 |  |  | (17"H X 33"W X 28"D) Hvac Equipment Ac-2 With Following Details; - Equipment Type: 4 Way Ceiling Cassette - Manf: Multiaqua, Model: Mhcfc4W-012-01 - Rating: 1.5 Ton, Total Cooling Capacity: 18,000 Btuh - Supply Air Flow: 870 Cfm, Water Flow Rate: 7.8 Gpm - Attached To Concrete Slab With 3/8"-16 Anvil (Fig 146)Threaded Rod (04 Ea), Hanger Mount Vibration Isolator; Spring Solator Type Mason Or Approved Equal (04 Ea) And 3/8" Hilti Hdi-P Drop In Anchor (04 Ea) - Factory Attached Fan Leg Clips (04 Ea) | EA | 1 | 0% | 1 | 4137 | 4137 | 2290 | 2290 | 6427
102 |  |  | (10"H X 44"W X 22"D) Hvac Equipment Ac-1 With Following Details; - Equipment Type: Ducted Fan Coil - Manf: Multiaqua, Model: Mhccw-10-00-01 - Rating: 02 Ton, Total Cooling Capacity: 24,800 Btuh - Supply Air Flow: 817 Cfm, Water Flow Rate: 10 Gpm - Attached To Concrete Slab With 3/8"-16 Anvil (Fig 146)Threaded Rod (08 Ea), Hanger Mount Vibration Isolator; Spring Solator Type Mason Or Approved Equal (04 Ea) And 3/8" Hilti Hdi-P Drop In Anchor (08 Ea) - (44" X 22") Drain Pan @ Bottom Of Unit Attached To Hangers | EA | 1 | 0% | 1 | 3906 | 3906 | 2133 | 2133 | 6039
103 |  |  | 44" Wide Air Filter @ Ac-3 | EA | 1 | 0% | 1 | 396 | 396 | 172 | 172 | 568
104 |  |  | Pressure Gauge With Needle Stop Valve | EA | 4 | 0% | 4 | 294 | 1176 | 162 | 648 | 1824
105 |  |  | Thermometer | EA | 4 | 0% | 4 | 213 | 852 | 104 | 416 | 1268
106 |  |  | 3/4" Drain Valve With Hose Bib | EA | 4 | 0% | 4 | 156 | 624 | 100 | 400 | 1024
107 |  |  | 1-1/4" Two Way Motorized Valve | EA | 2 | 0% | 2 | 235 | 470 | 128 | 256 | 726
108 |  |  | Balancing Valve | EA | 2 | 0% | 2 | 168 | 336 | 102 | 204 | 540
109 |  |  | Y Strainer | EA | 2 | 0% | 2 | 190 | 380 | 118 | 236 | 616
110 |  |  | Isolation Valve | EA | 4 | 0% | 4 | 166 | 664 | 105 | 420 | 1084
111 |  |  | Condensate Pump Cp-2 With Following Details; - Model Number: Vcmx-20Uls - Discharge Size: 1/4" Fnpt X 3/8" Od Barbed - Cord Length: 06 Feet, Weight: 5.5 Lb - It Will Have Automatic Start/Stop Capacity | EA | 1 | 0% | 1 | 2492 | 2492 | 1493 | 1493 | 3985
112 |  |  | Duct Mounted Diffuser/Grill With The Following Details; - Duct Size: 8" Dia, Cfm: 200 - Manf: Titus, Model: R-Omni | EA | 4 | 0% | 4 | 226 | 904 | 142 | 568 | 1472
113 |  |  | Duct Mounted Diffuser/Grill With The Following Details; - Duct Size: 8" Dia, Cfm: 225 - Manf: Titus, Model: R-Omni | EA | 2 | 0% | 2 | 241 | 482 | 150 | 300 | 782
114 |  |  | Duct Mounted Diffuser/Grill With The Following Details; - Duct Size: (14" X 14"), Cfm: 600 - Manf: Titus, Model: 350 Rl | EA | 1 | 0% | 1 | 338 | 338 | 190 | 190 | 528
115 |  |  | Duct Mounted Diffuser/Grill With The Following Details; - Duct Size: (6" X 6"), Cfm: 120 - Manf: Titus, Model: 350 Rl | EA | 1 | 0% | 1 | 205 | 205 | 130 | 130 | 335
116 |  |  | Provide Space Temperature Sensor And Provide Cat-6E To Existing Bms Panel | EA | 2 | 0% | 2 | 268 | 536 | 132 | 264 | 800
117 |  |  | (12" X 12") Access Door | EA | 1 | 0% | 1 | 331 | 331 | 168 | 168 | 499
118 |  |  | Provide Basnet Compatible Programmable Thermostat | EA | 2 | 0% | 2 | 214 | 428 | 137 | 274 | 702
SUB TOTAL | [7 empty] | Total Mat. Cost = | 78529.0451 | Total Lab. Cost = | 74287.1234 | 271816.1684 | 271816.1684
INSURANCE | [7 empty] | 5% |  |  |  | 13590.8084 | 13590.8084
OVERHEAD AND PROFIT | [7 empty] | 25% |  |  |  | 67954.0421 | 67954.0421
TOTAL BASE BID | [11 empty] | 353361.0189 | 353361.0189